- Please provide the required chilled-water flow rate, entering and leaving water temperatures, and any available mechanical drawings or equipment schedules for Building 1057. Chilled Water Supply Temp = 61, Chilled Water Return = 65, Chilled Water Flow GPM = Unknown. We can provide contractor drawings during project if they exist. The Chilled Water Supply & Return Temps were actual temps at time read.

- Should the contractor plan to reuse the existing electrical disconnect, breaker and wiring if they are compatible with the new chiller, or should the proposal include any required electrical modifications or upgrades? Plan to reuse per the SOW no electrical replacement will be conducted at this time.

- Please clarify the contractor’s responsibility for the BACnet controls. Is the scope limited to connecting the new chiller, or should it also include programming, point mapping and full integration with the existing building automation system? Will be required to be for the full automated system, will need to work with TekPlan the current BAC (DDC) contractor.

- What is the allowable chilled-water outage during the replacement? Will temporary cooling be required at any point during the project? There will be a temporary chiller on the building prior to replacement. During the outage, contractor will need to coordinate with CE to determine alternate work locations based on the contractors schedule.

- Is the piping and insulation scope limited to the modifications necessary to connect the new chiller, or should the proposal also include repairs to the existing deteriorated piping insulation and jacketing shown in the site photographs? Repairs and modifications should be for the connection to the new chiller and equipment that will ensure that the chiller runs efficiently.

- Will the existing concrete pad remain as-is? Please also advise of any special crane, rigging, site-access or base-entry requirements that must be included in our proposal. Yes the pad will remain. Base entry requirements are included in the SOW. There will need to be sufficient time to ensure if a crane is used that it is approved.

- Please confirm the required procedure for the refrigerant recovered from the existing chiller. Is the recovered refrigerant to be turned over to the Government, and if so, are there specific container or documentation requirements? Yes, refrigerant to be turned over to the government per the SOW. Contractor to supply recovery tank

- Please confirm whether there are any bonding, prevailing-wage, certified-payroll, security-clearance, badging, training or closeout requirements that must be included in our pricing. Other than what is required per attachments and terms and conditions – No.

- Can the bid date be extended a few days?  The site visit was today, and we need responses to the RFIs in order to provide an accurate quote? Extended till 24 September 2026 10:00am

- In executing this project, can one superintendent fulfill the supervision, safety, and QAQC roles? Yes

- Are contractors required to issue a contract specific QA/QC Plan? Yes

- Are contractors required to issue a contract specific Safety Plan? Yes

- Is this project tax exempt? Yes

- Can the sign in sheet be provided? The sign in sheet will not be provided at this time.

- Can you please verify the voltage? 460V/3PH/400A